## ASHRAE 90.1-2004
ASHRAE 90.1-2004 Baseline Fan Power Calculator
Constant Volume Fans (Systems 1 - 4)
<20,000 cfm Supply Air
|  | AHU name | Supply cfm | bhp | Pfan (watts) | W/cfm
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
≥20,000 cfm Supply Air
|  | AHU name | Supply cfm | bhp | Pfan (watts) | W/cfm
|  |  |  | 0.75 | 698.3357 | #DIV/0!
|  |  |  | 0.75 | 698.3357 | #DIV/0!
|  |  |  | 0.75 | 698.3357 | #DIV/0!
|  |  |  | 0.75 | 698.3357 | #DIV/0!
|  |  |  | 0.75 | 698.3357 | #DIV/0!
Variable Volume Fans (Systems 5 - 8)
<20,000 cfm Supply Air
|  | AHU name | Supply cfm | bhp | Pfan (watts) | W/cfm
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
|  |  |  | 0 | #NUM! | #NUM!
≥20,000 cfm Supply Air
|  | AHU name | Supply cfm | bhp | Pfan (watts) | W/cfm
|  |  |  | 1.5 | 1344.7902 | #DIV/0!
|  |  |  | 1.5 | 1344.7902 | #DIV/0!
|  |  |  | 1.5 | 1344.7902 | #DIV/0!
|  |  |  | 1.5 | 1344.7902 | #DIV/0!
|  |  |  | 1.5 | 1344.7902 | #DIV/0!

## ASHRAE 90.1-2007
ASHRAE 90.1-2007 Baseline Fan Power Calculator
Residential Fans (Systems 1 - 2)
| AHU Name | Baseline Supply Airflow (CFMS) | Pfan (watts) | W/cfm
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
Nonresidential Constant Volume Fans (Systems 3 - 4)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1.1B Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table 10.8 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Nonresidential Variable Volume Fans (Systems 5 - 8)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1.1B Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table 10.8 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Table 6.5.3.1.1B Fan Power Limitation Pressure Drop Adjustment
| Device |  |  |  | Adjustment
Credits
| Fully ducted return and/or exhaust air systems |  |  |  | 0.5 in. w.c.
| Return and/or exhaust airflow control devices |  |  |  | 0.5 in. w.c.
| Exhaust filters, scrubbers, or other exhaust treatment |  |  |  | The pressure drop of device calculated at fan system design condition
| Particulate Filtration Credit: MERV 9-12 |  |  |  | 0.5 in. w.c.
| Particulate Filtration Credit: MERV 13-15 |  |  |  | 0.9 in. w.c.
| Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters |  |  |  | Pressure drop calculated at 2x clean filter pressure drop at fan system design condition
| Carbon and other gas-phase air cleaners |  |  |  | Clean filter pressure drop at fan system design condition
| Heat recovery device |  |  |  | Pressure drop of device at fan system design condition
| Evaporative humidifier/cooler in series with another cooling coil |  |  |  | Pressure drop of device at fan system design condition
| Sound attenuation section |  |  |  | 0.15 in. w.c.
Deductions
| Fume Hood Exhaust Exception (required if 6.5.3.1.1 Exception [c] is taken) |  |  |  | -1.0 in. w.c.

## ASHRAE 90.1-2010
ASHRAE 90.1-2010 Baseline Fan Power Calculator
Residential Fans (Systems 1 - 2)
| AHU Name | Baseline Supply Airflow (CFMS) | Pfan (watts) | W/cfm
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
Heated Only Fans (Systems 9 - 10)
| AHU Name | Baseline Supply Airflow (CFMS) | Supply Fan Pfan (watts) | Supply Fan W/cfm | Baseline Non-Mechanical Cooling Airflow (CFMnmc) | Non-Mechanical Cooling Fan Pfan (watts) |  | Supply Fan W/cfm
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
Nonresidential Constant Volume Fans (Systems 3 - 4)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1.1B Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table 10.8 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
Nonresidential Variable Volume Fans (Systems 5 - 8)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1.1B Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table 10.8 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 85.5% | 0 | #DIV/0!
Table 6.5.3.1.1B Fan Power Limitation Pressure Drop Adjustment
| Device |  |  |  | Adjustment
Credits
| Fully ducted return and/or exhaust air systems |  |  |  | 0.5 in. w.c. (2.15 in. w.c. for laboratory and vivarium systems)
| Return and/or exhaust airflow control devices |  |  |  | 0.5 in. w.c.
| Exhaust filters, scrubbers, or other exhaust treatment |  |  |  | The pressure drop of device calculated at fan system design condition
| Particulate Filtration Credit: MERV 9-12 |  |  |  | 0.5 in. w.c.
| Particulate Filtration Credit: MERV 13-15 |  |  |  | 0.9 in. w.c.
| Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters |  |  |  | Pressure drop calculated at 2x clean filter pressure drop at fan system design condition
| Carbon and other gas-phase air cleaners |  |  |  | Clean filter pressure drop at fan system design condition
| Biosafety cabinet |  |  |  | Pressure drop of device at fan system design condition
| Energy Recovery Device, other than Coil Runaround Loop |  |  |  | (2.2 x Energy Recovery Effectiveness) - 0.5 in. w.c. for each airstream
| Coil Runaround Loop |  |  |  | 0.6 in. w.c. for each airstream
| Evaporative humidifier/cooler in series with another cooling coil |  |  |  | Pressure drop of device at fan system design condition
| Sound Attenuation Section |  |  |  | 0.15 in. w.c.
| Exhaust system serving fume hoods |  |  |  | 0.35 in. w.c.
| Laboratory and vivarium exhaust systems in high-rise buildings |  |  |  | 0.25 in. w.c./100 ft of vertical duct exceeding 75 ft

## ASHRAE 90.1-2013
ASHRAE 90.1-2013 Baseline Fan Power Calculator
Residential Fans (Systems 1 - 2)
| AHU Name | Baseline Supply Airflow (CFMS) | Pfan (watts) | W/cfm
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
Heated Only Fans (Systems 9 - 10)
| AHU Name | Baseline Supply Airflow (CFMS) | Supply Fan Pfan (watts) | Supply Fan W/cfm | Baseline Non-Mechanical Cooling Airflow (CFMnmc) | Non-Mechanical Cooling Fan Pfan (watts) |  | Supply Fan W/cfm
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
Nonresidential Constant Volume Fans (Systems 3 - 4, 12 - 13)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1-2 Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table 10.8-2 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Nonresidential Variable Volume Fans (Systems 5 - 8)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1-2 Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table 10.8-2 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Computer Room Variable Volume Fans (System 11)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1-2 Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table 10.8-2 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Table 6.5.3.1-2 Fan Power Limitation Pressure Drop Adjustment
| Device |  |  |  | Adjustment
Credits
| Fully ducted return and/or exhaust air systems |  |  |  | 0.5 in. w.c. (2.15 in. w.c. for laboratory and vivarium systems)
| Return and/or exhaust airflow control devices |  |  |  | 0.5 in. w.c.
| Exhaust filters, scrubbers, or other exhaust treatment |  |  |  | The pressure drop of device calculated at fan system design condition
| Particulate Filtration Credit: MERV 9-12 |  |  |  | 0.5 in. w.c.
| Particulate Filtration Credit: MERV 13-15 |  |  |  | 0.9 in. w.c.
| Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters |  |  |  | Pressure drop calculated at 2x clean filter pressure drop at fan system design condition
| Carbon and other gas-phase air cleaners |  |  |  | Clean filter pressure drop at fan system design condition
| Biosafety cabinet |  |  |  | Pressure drop of device at fan system design condition
| Energy recovery device, other than coil runaround loop |  |  |  | (2.2 x Energy Recovery Effectiveness) - 0.5 in. w.c. for each airstream
| Coil Runaround Loop |  |  |  | 0.6 in. w.c. for each airstream
| Evaporative humidifier/cooler in series with another cooling coil |  |  |  | Pressure drop of device at fan system design condition
| Sound Attenuation Section (fans serving spaces with design background noise goals below NC35) |  |  |  | 0.15 in. w.c.
| Exhaust system serving fume hoods |  |  |  | 0.35 in. w.c.
| Laboratory and vivarium exhaust systems in high-rise buildings |  |  |  | 0.25 in. w.c./100 ft of vertical duct exceeding 75 ft
Deductions
| Systems without central cooling device |  |  |  | -0.6 in. w.c.
| Systems without central heating device |  |  |  | -0.3 in. w.c.
| Systems with central electric resistance heat |  |  |  | -0.2 in. w.c.

## ASHRAE 90.1-2016
ASHRAE 90.1-2016 Baseline Fan Power Calculator
Residential Fans (Systems 1 - 2)
| AHU Name | Baseline Supply Airflow (CFMS) | Pfan (watts) | W/cfm
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
|  |  | 0 | #DIV/0!
Heated Only Fans (Systems 9 - 10)
| AHU Name | Baseline Supply Airflow (CFMS) | Supply Fan Pfan (watts) | Supply Fan W/cfm | Baseline Non-Mechanical Cooling Airflow (CFMnmc) | Non-Mechanical Cooling Fan Pfan (watts) |  | Supply Fan W/cfm
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
|  |  | 0 | #DIV/0! |  | 0 |  | #DIV/0!
Nonresidential Constant Volume Fans (Systems 3 - 4, 12 - 13)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1-2 Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table G3.9.1 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Nonresidential Variable Volume Fans (Systems 5 - 8)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1-2 Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table G3.9.1 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Computer Room Variable Volume Fans (System 11)
| AHU Name | Baseline Supply Airflow (CFMS) | Table 6.5.3.1-2 Pressure Drop Adjustment (PD) | Design Airflow Through Device (CFMD) | A | bhp | Lookup Table Row | Table G3.9.1 Fan Motor Efficiency | Pfan (watts) | W/cfm
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[5 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Table 6.5.3.1-2 Fan Power Limitation Pressure Drop Adjustment
| Device |  |  |  | Adjustment
Credits
| Return or exhaust systems required by code or accreditation standards to be fully ducted, or systems required to maintain air pressure differentials between adjacent rooms |  |  |  | 0.5 in. w.c. (2.15 in. w.c. for laboratory and vivarium systems)
| Return and/or exhaust airflow control devices |  |  |  | 0.5 in. w.c.
| Exhaust filters, scrubbers, or other exhaust treatment |  |  |  | The pressure drop of device calculated at fan system design condition
| Particulate Filtration Credit: MERV 9-12 |  |  |  | 0.5 in. w.c.
| Particulate Filtration Credit: MERV 13-15 |  |  |  | 0.9 in. w.c.
| Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters |  |  |  | Pressure drop calculated at 2x clean filter pressure drop at fan system design condition
| Carbon and other gas-phase air cleaners |  |  |  | Clean filter pressure drop at fan system design condition
| Biosafety cabinet |  |  |  | Pressure drop of device at fan system design condition
| Energy recovery device, other than coil runaround loop |  |  |  | For each airstream [(2.2 x Enthalpy Recovery Ratio) - 0.5] in. w.c.
| Coil Runaround Loop |  |  |  | 0.6 in. w.c. for each airstream
| Evaporative humidifier/cooler in series with another cooling coil |  |  |  | Pressure drop of device at fan system design condition
| Sound Attenuation Section (fans serving spaces with design background noise goals below NC35) |  |  |  | 0.15 in. w.c.
| Exhaust system serving fume hoods |  |  |  | 0.35 in. w.c.
| Laboratory and vivarium exhaust systems in high-rise buildings |  |  |  | 0.25 in. w.c./100 ft of vertical duct exceeding 75 ft
Deductions
| Systems without central cooling device |  |  |  | -0.6 in. w.c.
| Systems without central heating device |  |  |  | -0.3 in. w.c.
| Systems with central electric resistance heat |  |  |  | -0.2 in. w.c.

## Motor Efficiencies (hidden)
Row | Motor Horsepower | Minimum Nominal Full-Load Efficiency | 90.1-2010 Minimum Nominal Full-Load Efficiency
1 | 999999 | 95 | 96.2
2 | 200 | 95 | 96.2
3 | 150 | 95 | 95.8
4 | 125 | 94.5 | 95.4
5 | 100 | 94.5 | 95.4
6 | 75 | 94.1 | 95.4
7 | 60 | 93.6 | 95
8 | 50 | 93 | 94.5
9 | 40 | 93 | 94.1
10 | 30 | 92.4 | 93.6
11 | 25 | 92.4 | 93.6
12 | 20 | 91 | 93
13 | 15 | 91 | 92.4
14 | 10 | 89.5 | 91.7
15 | 7.5 | 89.5 | 91.7
16 | 5 | 87.5 | 89.5
17 | 3 | 87.5 | 89.5
18 | 2 | 84 | 86.5
19 | 1.5 | 84 | 86.5
20 | 1 | 82.5 | 85.5