## Slide 1
This information with automatically populate from EAp3. If you need to make changes, make them in EAp3. If the information does not auto-populate correctly, contact GBCI. If the EAp3 and EAc5 forms are different version numbers, you may need to upgrade one of the forms so that they populate correctly.
STEP 1: Make sure Table L-3 has been auto-populated correctly from EAp3.

## Slide 2
Auto-populated
Default values
Auto-calculated

## Slide 3
N = # of units of that type in the building
Q = tons of refrigerant per unit
STEP 2: Complete Table EAc5-1.

## Slide 4
Rc = refrigerant charge (lbs of refrigerant per ton of cooling capacity
Life = equipment life. Use default values from the LEED-EBOM Reference Guide. Alternative values can used only if documentation is provided to verify the claim.

## Slide 5
The actual leakage rate must be measured. Input the lbs of refrigerant that were added since the last time it was needed, the Lbs of refrigerant at full change, and the days since refrigerant was last added. The leakage rate Lr (%) will auto-calculate. Note that the minimum allowable leakage rate is 0.5% even if the actual value is less than that.
If days since refrigerant last added is >365, use 365.

## Slide 6
Mr (%) = end-of-life refrigerant loss. Assumed to be 10% for all equipment types, unless documentation is provided to justify an alternative value (such as manufacturer’s 30-year guarantee)

## Slide 7
Step 3: Confirm the information provided is accurate. Confirm that fire suppression systems do not use ozone-depleting substances.