<Building Name >

Systems Narrative Template

***HOW TO USE THIS TEMPLATE***

The following template provides a structure for developing a systems narrative compliant with LEED for Existing Buildings: Operations and Maintenance (LEED-EBOM) requirements. When completed properly, this document can be submitted as evidence of compliance with EAp1.

The process for customizing this template for a specific property includes:

- Reviewing sample language and additional guidance indicated in green. Sample language is provided for illustration purposes only and all content must be customized for your building.

- Inputting basic project-specific data where indicated in red (e.g., building name, name of responsible parties, etc.)

- The following building systems must be included as applicable to the building:

- Space heating

- Space cooling

- Ventilation

- Domestic water heating

- Humidification and/or dehumidification

- Lighting

- Building systems controls and building automation

General Guidance:

A general, summary description of each of the above base building systems installed in the project building is required. The narrative includes summaries of the central plant, distribution, and terminal units, as applicable. The narrative also includes all the controls associated with these systems, i.e., central automatic, local automatic, or occupant control. The narrative accounts for any differences in system types for different portions of the project building, i.e., for different floors, for interior vs. perimeter zones, etc.

In the systems narrative, it is not necessary to list each specific base building system explicitly (i.e., not each and every chiller), only each distinct type of system within the general types listed above (i.e., group all chillers having the same basic design and specifications). Other types of systems than those listed above, e.g., process equipment, office equipment, plumbing systems, fire protection systems, etc., may be included in the narrative if desired but are not required for LEED-EB: O&M compliance.

Heating and Cooling

Key Questions to Answer:

1. How are heating and cooling supplied to occupied spaces (i.e. district plant, central plant, package AHUs)?

2. Are there dedicated systems that supply heating or cooling to unique spaces in the building (i.e. perimeter spaces, data centers, retail)?

3. What are the major pieces of equipment used for heating and cooling?

4. How are heating and cooling delivered to occupied spaces (i.e. VAV, dual duct, constant volume, fan coils)

Example:

Heating and cooling for the building is provided by four constant volume dual deck air handling systems. For each of the four supply fans, the hot deck is heated with city-supplied steam and the cold deck is cooled with building generated chilled water. Operation of the supply fans is based on an occupied schedule of 6:30 am to 6:00 pm Tuesday through Friday and a start time of 6:00 am on Mondays during the heating season, as determined by current weather conditions. During cooling season a start time of 5:30 am Tuesday through Friday with a start time of 4:30 am on Mondays. All supply fans and associated equipment are disabled on weekends and holidays.

The chilled water system consists of one (1) 600 cooling ton Trane CVHE 3 stage centrifugal chiller, with associated chilled water pumps, condenser water pumps and one (1) two stage cooling tower. The system supplies chilled water to all fan unit cold deck coils for building cooling.

City-supplied steam is delivered to the building heating systems including the hot deck of the building air handling systems and heating water radiator systems serving perimeter spaces of the north, east, south and west sides of the building.

Ventilation

Key Questions to Answer:

1. How do the basic components of the ventilation system work including supply, exhaust, and return air.

2. Is the system variable air volume or constant volume?

3. What are the primary pieces of ventilation equipment?

4. What conditions are required for the system including air temperature and damper positions.

Example:

Building ventilation is provided by four (4) supply fans, each consisting of one (1) 100 hp supply fan with interlocked and sequenced return air, exhaust air, and outside air dampers and two (2) control interlocked 10 hp return air fans. Each supply fan is enabled by a signal from the BAS (based on the occupied schedule). Upon startup, the outside air and exhaust air dampers shall go to their minimum position. The mixed air temperature sensor shall modulate the economizer dampers to maintain a mixed air temperature of 60 degrees when the average zone temp is >72 degrees or maintain a mixed air temperature of 70 degrees when the average zone temp is < 70 degrees. The two return air fans shall be enabled. When the chiller plant is enabled, the unit dampers shall go to their minimum position.

Domestic Hot Water

Key Questions to Answer:

1. How is domestic hot water supplied to building spaces and what equipment is used for heating hot water.

Example:

City-supplied steam is delivered to the building domestic hot water systems. The system consists of one (1) self contained package system. The system is equipped with two 5 hp pumps with separate motors and an integral control panel. The domestic water pumping system is powered at all times. The pumps are started and stopped by the low pressure and high pressure switches built into the control panel. The controller allows for lead-lag pump operation.

Lighting

Key Questions to Answer:

1. What is the lighting mix within the building (i.e. T-8, T-8 low wattage, LED)?

2. How is lighting controlled in common spaces and in tenant spaces?

Low wattage T-8 lighting is used throughout the building and is augmented with task lighting as needed for occupant work stations. Lighting in common areas are controlled via occupancy sensors and tenant lighting is controlled manually. All tenant lighting is turned off in the evening by the building janitorial staff.

Controls

Key Questions to Answer:

1. What systems does the BAS control?

2. Does the BAS integrate with pneumatic or DDC controls?

The building automation system (BAS) is made by Special Magic Controls, which is a proprietary system. The BAS control the start and stop of the air handlers, condenser and chilled water pumps, and the chiller. The BAS provides remote monitoring for controlled systems.

Equipment Summary

Include an equipment summary/list if desired. This information is not required.