### Example Preventative maintenance Narrative

The building ventilation systems are maintained according to the operations and maintenance manual, which is based on ASHRAE 62.1-2010 Section 8. See specific details for each component of Section 8 below.

| ASHRAE 62.1-2010 Section | Description |
| --- | --- |
| 8.2 O&M Manual | 222 Anywhere Avenue maintains a building operations and maintenance manual. Preventative maintenance activities are performed according to this manual. |
| 8.3 Ventilation System Operation | The ventilation systems provide ventilation in accordance with Section 6 of ASHRAE 62.1-2010 |
| 8.4.1.1 Filters | Filters are changed for all ventilation systems annually or as needed based on the measured static pressure drop as recommended by the filter manufacturer; pressure drop is checked monthly |
| 8.4.1.2 Outdoor Air Dampers | Damper positions and function are checked per the manual (every 3 – 6 months) |
| 8.4.1.3 Humidifiers | No humidification in the building systems |
| 8.4.1.4 Dehumidification Coils | Cooling coils cleaned according to the manual (every 6 months) |
| 8.4.1.5 Drain Pans | Cleaned according to the manual (every 6 months) |
| 8.4.1.6 Outdoor Air Intake | Checked for cleanliness and integrity (every 6 months) |
| 8.4.1.7 Sensors | DDC system operation checked (every 6 months) |
| 8.4.1.8 Outdoor Airflow Verification | Outdoor airflow is measured concurrent with testing and balancing activities conducted every 5 years or during building equipment retrofits |
| 8.4.1.9 Cooling Towers | Cooling towers maintained to limit growth of biological contaminants |
| 8.4.1.10 Equipment Accessibility | All ventilation system equipment rooms kept free and clear (every 3 months) |
| 8.4.1.11 Floor Drains | Maintained according to the manual (every 3 months) |
| 8.4.2 Microbial Contamination | Comprehensive IAQ audit conducted every 2 years. Visual check of contamination via daily rounds |
| 8.4.3 Water Intrusion | Comprehensive IAQ audit conducted every 2 years. Visual check of contamination via daily rounds |