[image: image1.png]0) LEEDuser





Instructions: This sample plan is applicable to LEED projects using the Option D: Calibrated Simulation path. Sections in red are specifically intended to be filled in with project-specific information. However, if you use this template for your project, review every piece for applicability to your project, and add or modify pieces as needed.

Measurement & Verification Plan

LEED-(Rating System)
Overview

1.1 Project Background

The (project name) in (location) has been designed and constructed according to LEED-(Rating System) criteria. The project building is a new construction, (add project description). 

For addition information about the project design, please reference the following:

· Owner’s Project Requirements

· Mechanical Systems Narrative and Basis of Design

1.2 M&V Objectives

This Measurement and Verification (M&V) plan is based on Option D: Calibrated Simulation of the International Performance Measurement & Verification Protocol (IPMVP) Volume III: Concepts and Options for Determining Energy Savings in New Construction, April, 2003. The plan is intended to verify the cost savings associated with energy efficiency measures incorporated into the design, and to provide a recalibrated energy model that will serve as a tool for building operators in identifying and remedying causes of underperformance. Energy conservation measures (ECMs) found to deliver anticipated savings will be considered by (owner) for inclusion in architecture and design standards for future builds of similar properties.

The plan describes the process and responsible parties for:

· Predicting energy use by end use in the project building

· Measuring energy use by end use in the project building

· Calculating actual cost savings

· Corrective action when underperformance occurs

1.2 Baseline and Expected Energy Savings

Anticipated annual savings are based on energy modeling performed during the design process using (add software), which showed a building-wide reduction in energy costs of (savings %) compared to ASHRAE 90.1-(2004 or 2007)  efficiency levels. This projection was developed based on the Building Performance Rating Method in Appendix G of ASHRAE  90.1-(2004 or 2007)  , and is shown in the table below.

Table 1: Expected Annual Energy Savings
	Energy Type
	Baseline Annual Consumption (kBtu)
	Projected Annual Consumption (kBtu)
	Projected Annual Savings (kBtu)
	Projected Annual Cost Savings ($)
	Percent Cost Savings

	Electricity
	
	
	
	
	

	Natural Gas
	
	
	
	
	

	Total
	
	
	
	
	


The expected annual consumption values above will be adjusted based on weather data, occupancy levels, and system operating parameters realized during the year-long period during which energy consumption measurements are in place. The adjusted expected savings will then be compared to actual savings.
1.3 M&V Plan Summary

Through the use of (example language: utility invoices, building automation system (BAS) data logging, permanently installed sub-metering and spot measurements), the facility’s operations staff will work with the mechanical engineering design and commissioning firm, (company name), to measure the actual utility usage of the building and key end uses for two years of post-occupancy consumption. 

Collected data will be used to verify the predicted energy performance of energy conservation measures (ECMs) integrated into the design as part of the LEED effort. 

	Table 2: M&V Plan Summary

	ECM
	Description
	M&V Methods and Equipment

	Lighting
	(example)

Optimize activation using scheduling and occupancy sensors
	(example)

Monitor lighting electricity usage through use of sub meters

	Exterior Lighting
	(example)

Optimize activation using scheduling through time clocks and photocell
	(example)

Monitor lighting electricity usage through use of sub meters

	Space Heating
	(example)

Optimize activation using scheduling and remote thermostats
	(example)

Monitor space heating electricity usage through use of sub meters and BAS data logging.

	Space Cooling
	(example)

Optimize cooling through electronic thermostats and space sensors to minimize ventilation air
	(example)

Monitor space cooling electricity usage through use of sub meters and BAS data logging.

	Space Cooling
	(example)

Optimize cooling through electronic thermostats and space sensors to minimize ventilation air
	(example)

Monitor gas usage through gas sub meters and BAS data logging.

	Space Heating
	(example)

Optimize space temperature heating 
	(example)

Monitor gas usage through gas sub meters and BAS data logging.

	Water Heating
	(example)

Reduce hot water storage temperature 
	(example)

Monitor gas usage through gas sub meters


1.4 Equipment Commissioning

Commissioning activities occurred in the project building for the following energy-related systems prior to occupancy in (date). 
· Heating

· Ventilation

· Air conditioning

· Refrigeration

· Lighting

· Domestic hot water

· Controls

Commissioning was performed by (company name) in accordance to LEED EA Prerequisite 1, Fundamental Commissioning of the Building Energy Systems. The Commissioning Report is included in the LEED Certification Application, and records of deficiencies and their remediation of kept by (company name). Throughout the M&V period, minor additional commissioning activities will be performed as necessary by (company name) and the building operations staff.

1.5 M&V Period

The M&V period is the timeframe during which monthly readings of energy consumption will occur. This period shall be at least two years in length, and is anticipated to commence on (date). (The M&V period will vary according project-specific objectives. However, a minimum of two years is recommended for new construction projects.)
1.6 Expected M&V Accuracy

Permanent metering equipment will have Utility Grade Metering Accuracy and meet ANSI National Accuracy Standards.

Within the M&V program, it is expected that data collected during the period will be highly accurate. Limitations of the modeling program are expected to be the greatest potential source of inaccuracy. Adherence to ASHRAE 90.1-(2004 or 2007)  Appendix G protocols will be used to minimize this potential. The project is setting a goal of 5% error in the calibrated energy models.

(Include a description of how the project will evaluate accuracy during the M&V process. See ASHRAE Guideline 14 for additional information. At minimum, a specific accuracy goal should be stated for the energy model calibration. In addition, include accuracies for other data collection activities if known.)

1.7 Quality Assurance

The M&V strategy will be reviewed following the first month of implementation to ensure that procedures and processes are effective for capturing the required data. Monthly data recordings will be reviewed promptly for anomalous values that could signal data errors or underperforming equipment.

1.8 Budget and Resources
(Owner) is financially responsible for executing the M&V program costs. Materials and labor budgets are outlined below. These do not reflect soft costs associated with data recording on the part of operations staff.

	Item
	Budget

	Submetering Equipment
	($15,000-$25,000)

	M&V Labor
	($20,000)

	Corrective Action
	As needed


1.0 Data and Assumptions

2.1 Energy Rate Data 

Electricity costs will be calculated using (project’s rate structure name) for (location) based on (utility provider).
Natural gas usage costs will be calculated using (project’s rate structure name) for (location) based on (gas utility company).
(It is extremely important to use the project’s actual rate structure in the calibrated energy models. If the project uses EIA published state averages for its LEED submission, they should be replaced during the model calibration)

2.1 Energy Savings Calculations

Energy savings will be determined by comparing measured energy use to the projected based on the following equation:

Energy Savings = Projected Baseline Energy Use – Measured Post-Construction Energy Use

Measured Post-Construction Energy Use is the energy use of the as-built facility. This is in accordance with the Method 2, Option D: Savings Estimation protocol in the IPMVP standard.
2.2 Reporting Requirements

The M&V report shall be provided to (owner) within 45 days of the completion of the first and second years of M&V period. The owner or owner’s representative shall then review the report with a subsequent 30 days. The report will include summaries of logged information for each ECM, log deviations from expected savings, provide recommendations for corrective actions and future savings, and record any significant O&M work performed on equipment associated with ECMs. 

2.3 Responsible Parties

(Company name or in-house staff department) is the entity primarily responsible for the M&V Plan’s development, coordination and implementation. The project owner and building operations staff will support implementation of the plan.

	Table 3: M&V Responsibilities

	M&V Activity
	Responsible Party

	Baseline energy model
	XX

	Recalibrate baseline energy model to reflect as-built and post-occupancy conditions
	XX

	Identification of ECMs for inclusion in the M&V plan
	XX

	Development of M&V plan
	XX

	Compilation of all occupancy, controls, BAS data, and scheduling information during the M&V period
	XX

	Spot metering during M&V period
	XX

	Installation of required sub-metering equipment
	XX

	M&V Report
	XX

	Corrective Action
	XX


2.0 Electricity M&V Plan

3.1 Electricity Baseline Simulation

IPMVP Option D has been selected for the M&V plan because a) the integrated design process yielded efficiency strategies intended to work in concert with each other, making isolation of ECMs inappropriate, and b) a computer simulation was used during the design phase to predict whole building energy usage. The computer simulation was performed using (software) to demonstrate achievement with LEED-(Rating System) EA Credit 1: Optimize Energy Performance. Model inputs are recorded in the LEED Certification Application materials. The (software) energy model files have been supplied to (owner) and are available for calibration.
The energy analysis used climatic data for (location), which is proximate and climatically similar to (project location). 
Building occupancy and operating schedules will be estimated by (e.g., occupant surveys). 

 3.2 Electricity Baseline and Expected Usage Projections

The projected baseline is based on the minimum requirements of ASHRAE 90.1-(2004 or 2007) for buildings with similar mechanical systems.

Projections reflect annual electricity consumption, and are summarize by end use in the table below.

Table 4: Baseline an Expected Electricity Usage Projects by End Use

	End Use
	Baseline Annual Electricity (kWh)
	Expected Annual Electricity (kWh)
	Actual Annual Electricity (kWh)

	Interior Lighting, Exterior Lighting (tradable and non tradable)


	397,274
	228,873
	TBD

	Space Heating
	191,956
	159,413
	TBD

	Space Cooling
	160,231
	117,992
	TBD

	Fans – Interior
	120,403.8
	68,973
	TBD

	Guestroom Power, lighting and HVAC
	228,335
	228,335
	TBD


3.3 Post-Installation Equipment Monitoring

Following installation and before occupancy, commissioning activities were used to verify the proper fundamental operations of the building systems. Should a component of an ECM fail to work in the designed manner, maintenance will be performed to restore the equipment to its designed operation. Permanent and spot metering will be used to measure electrical consumption. Operation staff will use metered trend data and spot checks to identify underperforming systems so that corrective action can be taken. 

The method of metering will be through sealed electronic sub meters, these meters will record the electrical loads indicated within this plan. These meters are intended to validate the anticipated energy savings previously indicated in LEED EAc1 and as indicated below. Recalibration of the meters can be done by sending these meters back to the factory, contacts with these vendors have indicated that this is typically done every five years. The table below shows the metering strategy that will be used to monitor electrical loads.

	Table 5: Electrical Metering Equipment

	Meter
	Location
	Metered Panels/Loads
	Load Type
	Loads

	M1
	ELECTRICAL ROOM 
	PANEL EM-A – METER CIRCUIT BREAKER FEEDING PANEL OLP – METER TO BE RATED FOR 100AMPS 
	Electric - Exterior Lighting (tradable and non tradable)
	OUTDOOR LIGHTING

	
	
	
	
	

	M1-A 

Using meter M! add additional CTs to read the energy usage
	ELECTRICAL ROOM 
	PANEL LP-1A, LP-1B, LP-2, LP-3, LP-4 AND DIMMING PANEL TO SUBTRACT LOAD FOR PANEL MECH 1B
	Electric - Interior LIGHTING 


	INTERIOR LIGHTING

	
	
	
	
	

	M1-B

Using meter M1 add additional CTs to read the energy usage
	ELECTRICAL ROOM 
	PANEL EM-1 – METER TO BE RATED AT 200AMPS
	Electric - INTERIOR LIGHTING


	LIGHTING



	M2
	ELECTRICAL ROOM 
	PANEL MECH-1A –METER TO BE RATED FOR 1600AMPS. PROVIDE XTRA SET OF CT’S TO SUBTRACT LOAD FOR PANEL MECH 1B
	Electric - Space Cooling 


	INTERIOR COOLING EQUIPMENT ROOF TOP UNITS AND SPLIT SYSTEMS

	
	
	
	
	

	M3
	ELECTRICAL ROOM 
	PANEL MECH-1B –METER TO BE RATED FOR 400AMPS. PROVIDE CT’S TO PICK UP SPACE HEATING
	Electric - Space HEATING


	INTERIOR WALL AND CABINET HEATERS



	
	
	
	
	

	M4
	ELECTRICAL ROOM
	PANEL MECH-1B –METER TO BE RATED FOR 400AMPS. PROVIDE CT’S TO PICK UP SPACE COOLING
	Electric - Space COOLING


	SPLIT SYSTEM AC EQUIPMENT FED FROMTHIS PANEL



	M5
	ELECTRICAL ROOM
	PANEL MECH-1B –METER TO BE RATED FOR 400AMPS. PROVIDE CT’S TO PICK UP SPACE HEATING
	Electric - Space HEATING


	INTERIOR WALL AND CABINET HEATERS



	
	
	
	
	

	M6
	ELECTRICAL ROOM
	PANEL MDP, METER CIRCUIT BREEAKERS FEEDING PANEL 1GB, 2GA, 2GB, 3GA, 3GB,4GA AND 4GB – METER TO BE RATED AT 1200AMPS
	Electric - Guestroom Power, lighting and HVAC
	LIGHTING, POWER AND HVAC IN GUESTROOM




The BAS includes data logging functions that will also be used to provide ongoing measurement and verification data pertaining to certain mechanical systems. BAS data will be used in conjunction with metered electricity to track equipment performance, identify underperforming systems. This data will also be used to assist the baseline energy model recalibration. The table below shows the metering strategy that will be used to monitor mechanical systems that use electricity.

	Table 6: BAS Monitoring Summary – Electrical

	Item
	Meter Type
	Description/Intended Use

	Individual HVAC motors, constant speed.
	Run Time 
	The BAS provides start/stop contacts and calculates run time to all constant load HVAC motors. Power consumption can be calculated from run time and power measured during balancing.

	Individual HVAC motors, variable speed
	Run time and VFD speed
	The BAS provides start/stop contacts and calculates run time to all variable speed HVAC motors. Power consumption can be calculated from run time and speed output to VF drive from DDC system.

	Building cooling load
	Flow meter and temperature sensors
	Overall building cooling load is continuously metered by the BAS via a BTU meter on the chilled water system.

	Air distribution static pressures
	Duct pressure sensor
	Monitored through the BAS system.

	Ventilation Air Volume
	Air Flow Station
	Monitored through the BAS system.


Please note that the exhaust fans run continuously (due to fire life safety codes); spot checking will occur on a monthly basis to validate energy usage. The usage of the fans is independent of the environment or guest room occupancy.

Building occupancy and operating schedules will be estimated by (e.g., occupant surveys) and Building Automation System data. 

3.4 M&V Period Verification Activities (Update to reflect strategies)

On a monthly basis, operations staff shall record the energy consumption of loads associated with ECMs. Also record any significant O&M activities performed on the systems during that time period, including any associated costs. At the end of the two-year M&V period, summarize the electrical consumption data for comparison with the recalibrated baseline and expected consumption. The metered equipment shall be inspected at the conclusion of the M&V period and as needed to verify proper operation. All collected information and comparison results will be included in the M&V report.

All efforts will be made to prevent the omission or loss of metered data. In the event that data is missing or lost, existing data from before and after the missing portion will be used to extrapolate if appropriate. Extension of the M&V period is also an option for mitigating the effect of lost data.
Table 6: Electrical Monthly Consumption Reporting Form

	Measurements Recorded By:
	

	Date of Measurements:
	

	Occupancy Levels:
	

	Meter 
	Location
	Electric Consumption (kWh)
	O&M Activities / Costs / Comments

	M1


	Electrical Room 
	
	

	M2


	Electrical Room 
	
	

	M3


	Electrical Room 
	
	

	M4


	Electrical Room
	
	

	M5


	Electrical Room
	
	

	M6


	Electrical Room
	
	


3.0 Natural Gas M&V Plan

4.1 Natural Gas Baseline Simulation

IPMVP Option D has been selected for the M&V plan because a) the integrated design process yielded efficiency strategies intended to work in concert with each other, making isolation of ECMs inappropriate, and b) a computer simulation was used during the design phase to predict whole building energy usage. The computer simulation was performed using (software) to demonstrate achievement with LEED-(Rating System) EA Credit 1: Optimize Energy Performance. Model inputs are recorded in the LEED Certification Application materials. 

The energy analysis used climatic data for (location), which is proximate and climatically similar to (project location).
Building occupancy during the M&V period will be tracked based on guest room sales. Due to the nature of the building, operating hours are static.
 4.2 Natural Gas Baseline and Expected Usage Projections

The projected baseline is based on the minimum requirements of ASHRAE 90.1-(2004 or 2007)  for buildings with similar mechanical systems.

Projections reflect annual natural gas consumption, and are summarize by end use in the table below.

Table 7: Baseline an Expected Electricity Usage Projects by End Use

	End Use
	Baseline Annual Natural Gas (kBtu)
	Expected Annual Natural Gas (kBtu)
	Actual Annual Natural Gas (kBtu)

	Space Heating
	809,779.3
	904979
	TBD

	Service Water Heating - Domestic
	520,320.8
	339910
	TBD


4.3 Post-Installation Equipment Monitoring

Following installation and before occupancy, commissioning activities were used to verify the proper fundamental operations of the building systems. Should a component of an ECM fail to work in the design manner, maintenance will be performed to restore the equipment to its designed operation. Permanent and spot metering will be used to measure electrical consumption. Operation staff will use metered trend data and spot checks to identify underperforming systems so that corrective action can be taken. 

Gas meters will be turbine style. Recalibration of the meters can be done by sending these meters back to the factory, contacts with these vendors have indicated that this is typically done every five years. The table below shows the metering strategy that will be used to monitor natural gas loads.

Table 8: Natural Gas Metering Equipment
	Meter
	Location
	Metered Loads
	Load Type
	Loads

	Space Heating
	Roof Top Equipment
	RTU-1, RTU-2, RTU-3 and RTU-4
	Gas
	Roof Top Equipment

	Service Water Heating - Domestic
	Mechanical Room 
	GWH-1 (750mbh)
	Gas
	Hot Water


The BAS includes data logging functions that will also be used to provide ongoing measurement and verification data pertaining to certain mechanical systems. BAS data will be used in conjunction with metered electricity to track equipment performance, identify underperforming systems. This data will also be used to assist the baseline energy model recalibration. The table below shows the metering strategy that will be used to monitor mechanical systems that use natural gas.

	Table 6: BAS Monitoring Summary – Gas

	Item
	Meter Type
	Description/Intended Use

	Building heating load
	Flow meter and temperature sensors
	Overall building heating load is continuously metered by the BAS via a BTU meter on the hot water system.


Building occupancy and operating schedules will be estimated by (e.g., occupant surveys) and Building Automation System data. 

4.4 M&V Period Verification Activities

On a monthly basis, operations staff shall record the energy consumption of loads associated with ECMs. Also record any significant O&M activities performed on the systems during that time period, including any associated costs. At the end of the two-year M&V period, summarize the natural gas consumption data for comparison with the recalibrated baseline and expected consumption. The metered equipment shall be inspected at the conclusion of the M&V period and as needed to verify proper operation. All collected information and comparison results will be included in the M&V report.

All efforts will be made to prevent the omission or loss of metered data. In the event that data is missing or lost, existing data from before and after the missing portion will be used to extrapolate if appropriate. Extension of the M&V period is also an option for mitigating the effect of lost data.
Table 9: Natural Gas Monthly Consumption Reporting Form

	Measurements Recorded By:
	

	Date of Measurements:
	

	Occupancy Levels:
	

	Meter 
	Location
	Natural Gas Consumption (kBta)
	O&M Activities / Costs / Comments

	G1
	Roof Top Equipment
	
	

	G2
	Mechanical Room 
	
	


[image: image2.png]wwwleeduser.com

Pusished by BuldingGreen, LLC + 122 Blrge Street, Brattieboro, VT 05301 + (802) 257-7300.





[image: image1.png][image: image2.png]