LEED Flush-Out Procedure

The flush-out occurred after construction and all interior furnishings were installed. (construction ended in November 2019, all interior furnishings were installed during Dec 2019 and Jan 2020) Occupancy is expected to occur in June.

Permanent air handling units were used to flush-out the building. All temporary filters and duct coverings installed as part of the construction IAQ management plan were removed prior to the flush-out.

Prior to the flushout new MERV 13 filters were installed at all units.

All ventilation units (and exhaust fans) were energized at 7am on Saturday, February 1st.

During the flush-out period, the internal temperature of the building did not fall below 60 degrees F or above 80 degrees F and the internal relative humidity of the building did not exceed 60% RH.  Heating/cooling has sequenced as necessary to maintain the lower temperature limit and upper humidity level during the flushout.

All internal doors were open to ensure air flow through all occupiable spaces and prevent short circuiting of air flow.  All exhaust fans operated during the flush-out period to help prevent short circuiting of air.

On Friday, March 13th at 4pm the ventilation/exhaust systems were taken out of ‘flushout’ mode, all filters were replaced with new MERV 13 filters, and the ventilation/exhaust systems were put back into normal operating mode.

The flushout occurred for a total of 41+ days.