## Instructions
Minimum Indoor Air Quality Performance Calculator LEED 2009 and v4 EQ Prerequisite Minimum Indoor Air Quality Performance
Step 1.
Enable macros.
Note: This calculator is for use with Excel for Mac 2011 and Excel 2007 or later.
Step 2.
| Unit of measurement | [5 empty] | IP units
Note: This selection must match the unit of measurement chosen during project registration.
Step 3.
| LEED rating system version | [5 empty] | LEED v4
Note: This selection must match project registration.
Step 4.
| Increase breathing zone outdoor airflow by 30%? | [5 empty] | Yes
Select if attempting EQ Credit Enhanced Indoor Air Quality Strategies, Option 2, Strategy B: Increased Ventilation.
Step 5.
Single Zone Systems
| Does the project include single zone systems? | [5 empty] | No
Multiple Zone and 100% Outdoor Air Systems
Add a tab for each multiple zone and 100% outdoor air system in the project using the "Add System" button below.
Step 6.
Complete the ventilation rate procedure (VRP) for each ventilation system, at the specified analysis condition.
Step 7.
Upload the completed spreadsheet to LEED Online. Complete any related summary fields in the LEED credit form with the results of the calculator.
Assumptions
Zone Air Distribution Effectiveness (Ez)
Code |  | Air Distribution Configuration |  |  |  |  | Ez
CS |  | Ceiling supply of cool air |  |  |  |  | 1
CSFR |  | Ceiling supply of warm air and floor return |  |  |  |  | 1
CSCRH |  | Ceiling supply of warm air 15°F (8°C) or more above space temperature and ceiling return |  |  |  |  | 0.8
CSCRW |  | Ceiling supply of warm air less than 15°F (8°C) above space temperature and ceiling return provided that the 150 fpm (0.8 m/s) supply air jet reaches to within 4.5 ft (1.4 m) of floor level. Note: For lower velocity supply air, Ez = 0.8. |  |  |  |  | 1
FSCR |  | Floor supply of cool air and ceiling return provided that the 150 fpm (0.8 m/s) supply jet reaches 4.5 ft (1.4 m) or more above the floor. Note: Most underfloor air distribution systems comply with this proviso. |  |  |  |  | 1
FSCR-LV |  | Floor supply of cool air and ceiling return, provided low-velocity displacement ventilation achieves unidirectional flow and thermal stratification |  |  |  |  | 1.2
FSFR |  | Floor supply of warm air and floor return |  |  |  |  | 1
FSCRW |  | Floor supply of warm air and ceiling return |  |  |  |  | 0.7
MUEX |  | Makeup supply drawn in on the opposite side of the room from the exhaust and/or return |  |  |  |  | 0.8
MU-EX |  | Makeup supply drawn in near to the exhaust and/or return location |  |  |  |  | 0.5
Source: ASHRAE 62.1, Table 6-2
System Ventilation Efficiency (Ev)
Max Zp |  | Ev
<=0.15 |  | 1
<=0.25 |  | 0.9
<=0.35 |  | 0.8
<=0.45 |  | 0.7
<=0.55 |  | 0.6
>0.55 |  | use Appendix A
Source: ASHRAE 62.1, Table 6-3
Zone Secondary Recirculation Fraction (Er)
System Configuration | [6 empty] | Er
Plenum return systems with secondary recirculation (e.g., fan-powered VAV with plenum return) | [6 empty] | <1.0
Ducted return systems with secondary recirculation (e.g., fan-powered VAV with ducted return) | [6 empty] | 0
Systems with system-level recirculation (e.g., dual-fan dual-duct systems with ducted return) | [6 empty] | 1
Other system types | [6 empty] | 0.75
Source: ASHRAE 62.1, Section A1.2.2
Occupancy
Occupancy Category |  |  | People OA Rate |  | Area OA Rate |  | Default Occupant Density (#/1000 sq ft or #/100 sq m) |  | 9= 2009 only 4=v4 only B= Both
|  |  | (cfm per person) | (l/s per person) | (cfm per sq ft) | (l/s per sq m)
Art classroom |  |  | 10 | 5 | 0.18 | 0.9 | 20 |  | B
Auditorium seating area |  |  | 5 | 2.5 | 0.06 | 0.3 | 150 |  | B
Bank vault / safe deposit |  |  | 5 | 2.5 | 0.06 | 0.3 | 5 |  | B
Banks or bank lobbies |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 15 |  | 4
Barbershop |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 25 |  | B
Barracks sleeping areas |  |  | 5 | 2.5 | 0.06 | 0.3 | 20 |  | B
Bars / cocktail lounges |  |  | 7.5 | 3.8 | 0.18 | 0.9 | 100 |  | B
Beauty and nail salon |  |  | 20 | 10 | 0.12 | 0.6 | 25 |  | B
Bedroom / living room |  |  | 5 | 2.5 | 0.06 | 0.3 | 10 |  | B
Booking / waiting |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 50 |  | B
Bowling alley (seating) |  |  | 10 | 5 | 0.12 | 0.6 | 40 |  | B
Break rooms (general) |  |  | 5 | 2.5 | 0.06 | 0.3 | 25 |  | B
Breakrooms (office buildings) |  |  | 5 | 2.5 | 0.12 | 0.6 | 50 |  | 4
Cafeteria / fast food dining |  |  | 7.5 | 3.8 | 0.18 | 0.9 | 100 |  | B
Cell |  |  | 5 | 2.5 | 0.12 | 0.6 | 25 |  | B
Classrooms (age 9 plus) |  |  | 10 | 5 | 0.12 | 0.6 | 35 |  | B
Classrooms (ages 5-8) |  |  | 10 | 5 | 0.12 | 0.6 | 25 |  | B
Coffee stations |  |  | 5 | 2.5 | 0.06 | 0.3 | 20 |  | B
Coin-operated laundries |  |  | 7.5 | 3.8 | 0.12 | 0.6 | 20 |  | B
Common corridors |  |  | 0 | 0 | 0.06 | 0.3 | 0 |  | B
Computer (not printing ) |  |  | 5 | 2.5 | 0.06 | 0.3 | 4 |  | B
Computer lab |  |  | 10 | 5 | 0.12 | 0.6 | 25 |  | B
Conference / meeting |  |  | 5 | 2.5 | 0.06 | 0.3 | 50 |  | B
Corridors |  |  | 0 | 0 | 0.06 | 0.3 | 0 |  | B
Courtrooms |  |  | 5 | 2.5 | 0.06 | 0.3 | 70 |  | B
Day room |  |  | 5 | 2.5 | 0.06 | 0.3 | 30 |  | B
Daycare (through age 4) |  |  | 10 | 5 | 0.18 | 0.9 | 25 |  | B
Daycare sickroom |  |  | 10 | 5 | 0.18 | 0.9 | 25 |  | B
Disco / dance floors |  |  | 20 | 10 | 0.06 | 0.3 | 100 |  | B
Dwelling unit |  |  | 5 | 2.5 | 0.06 | 0.3 | n/a |  | 9
Dwelling unit - studio or one-bedroom |  |  | 5 | 2.5 | 0.06 | 0.3 | 2 |  | 4
Dwelling unit - three-bedroom |  |  | 5 | 2.5 | 0.06 | 0.3 | 4 |  | 4
Dwelling unit - two-bedroom |  |  | 5 | 2.5 | 0.06 | 0.3 | 3 |  | 4
Electrical equipment rooms |  |  | 0 | 0 | 0.06 | 0.3 | 0 |  | 9
Elevator machine rooms |  |  | 0 | 0 | 0.12 | 0.6 | 0 |  | 9
Gambling casinos |  |  | 7.5 | 3.8 | 0.18 | 0.9 | 120 |  | B
Game arcades |  |  | 7.5 | 3.8 | 0.18 | 0.9 | 20 |  | B
General manufacturing (excludes heavy industrial and processes using chemicals) |  |  | 10 | 5 | 0.18 | 0.9 | 7 |  | 4
Guard stations |  |  | 5 | 2.5 | 0.06 | 0.3 | 15 |  | B
Gym, stadium (play area) |  |  | 0 | 0 | 0.3 | 1.5 | 30 |  | B
Health club / aerobics |  |  | 20 | 10 | 0.06 | 0.3 | 40 |  | B
Health club / weight |  |  | 20 | 10 | 0.06 | 0.3 | 10 |  | B
Kitchen (cooking) |  |  | 7.5 | 3.8 | 0.12 | 0.6 | 20 |  | 4
Laundry rooms within dwelling units |  |  | 5 | 2.5 | 0.12 | 0.6 | 10 |  | B
Laundry rooms, central |  |  | 5 | 2.5 | 0.12 | 0.6 | 10 |  | B
Lecture classroom |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 65 |  | B
Lecture hall (fixed seats) |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 150 |  | B
Legislative chambers |  |  | 5 | 2.5 | 0.06 | 0.3 | 50 |  | B
Libraries |  |  | 5 | 2.5 | 0.12 | 0.6 | 10 |  | B
Lobbies |  |  | 5 | 2.5 | 0.06 | 0.3 | 150 |  | B
Lobbies / prefunction |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 30 |  | B
Main entry lobbies |  |  | 5 | 2.5 | 0.06 | 0.3 | 10 |  | B
Mall common areas |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 40 |  | B
Media center |  |  | 10 | 5 | 0.12 | 0.6 | 25 |  | B
Multi-purpose assembly |  |  | 5 | 2.5 | 0.06 | 0.3 | 120 |  | B
Multi-use assembly |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 100 |  | B
Museums (children's) |  |  | 7.5 | 3.8 | 0.12 | 0.6 | 40 |  | B
Museums / galleries |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 40 |  | B
Music / theater/ dance |  |  | 10 | 5 | 0.06 | 0.3 | 35 |  | B
Occupiable storage rooms for dry materials |  |  | 5 | 2.5 | 0.06 | 0.3 | 2 |  | 4
Occupiable storage rooms for liquids or gels |  |  | 5 | 2.5 | 0.12 | 0.6 | 2 |  | 4
Office space |  |  | 5 | 2.5 | 0.06 | 0.3 | 5 |  | B
Pet shops (animal areas) |  |  | 7.5 | 3.8 | 0.18 | 0.9 | 10 |  | B
Pharmacy (prep, area) |  |  | 5 | 2.5 | 0.18 | 0.9 | 10 |  | B
Photo studios |  |  | 5 | 2.5 | 0.12 | 0.6 | 10 |  | B
Places of religious worship |  |  | 5 | 2.5 | 0.06 | 0.3 | 120 |  | B
Reception areas |  |  | 5 | 2.5 | 0.06 | 0.3 | 30 |  | B
Restaurant dining rooms |  |  | 7.5 | 3.8 | 0.18 | 0.9 | 70 |  | B
Sales |  |  | 7.5 | 3.8 | 0.12 | 0.6 | 15 |  | B
Science laboratories |  |  | 10 | 5 | 0.18 | 0.9 | 25 |  | B
Shipping / receiving |  |  | 10 | 5 | 0.12 | 0.6 | 2 |  | B
Sorting, packing, light assembly |  |  | 7.5 | 3.8 | 0.12 | 0.6 | 7 |  | 4
Spectator areas |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 150 |  | B
Sports arena (play area) |  |  | 0 | 0 | 0.3 | 1.5 | 0 |  | B
Stages, studios |  |  | 10 | 5 | 0.06 | 0.3 | 70 |  | B
Storage rooms |  |  | 0 | 0 | 0.12 | 0.6 | 0 |  | 9
Supermarket |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 8 |  | B
Swimming (pool & deck) |  |  | 0 | 0 | 0.48 | 2.4 | 0 |  | B
Telephone / data entry |  |  | 5 | 2.5 | 0.06 | 0.3 | 60 |  | B
Telephone closets |  |  | 0 | 0 | 0 | 0 | 0 |  | 4
Transportation waiting |  |  | 7.5 | 3.8 | 0.06 | 0.3 | 100 |  | B
University / college laboratories |  |  | 10 | 5 | 0.18 | 0.9 | 25 |  | 4
Warehouses |  |  | 10 | 5 | 0.06 | 0.3 | 0 |  | B
Wood / metal shop |  |  | 10 | 5 | 0.18 | 0.9 | 20 |  | B
v03
Copyright © 2012
U.S. Green Building Council
All Rights Reserved
Last updated 3 June 2016
[9 empty] | UOM | LEED | Credit
[9 empty] | 1 | 2 | 1
[9 empty] | 1 = IP, 2 = SI | 1 = 2009, 2 = v4 | 1 = yes, 2 = no
[9 empty] | LEED2009 | LEEDv4 | Single Zone
[9 empty] | Art classroom | Art classroom | 2
[9 empty] | Auditorium seating area | Auditorium seating area | 1 = yes, 2 = no
[9 empty] | Bank vault / safe deposit | Bank vault / safe deposit
[9 empty] | Barber shop | Banks or bank lobbies
[9 empty] | Barracks sleeping areas | Barbershop
[9 empty] | Bars / cocktail lounges | Barracks sleeping areas
[9 empty] | Beauty and nail salon | Bars / cocktail lounges
[9 empty] | Bedroom / living room | Beauty and nail salon
[9 empty] | Booking / waiting | Bedroom / living room
[9 empty] | Bowling alley (seating) | Booking / waiting
[9 empty] | Break rooms (general) | Bowling alley (seating)
[9 empty] | Cafeteria / fast food dining | Break rooms (general)
[9 empty] | Cell | Breakrooms (office buildings)
[9 empty] | Classrooms (age 9 plus) | Cafeteria / fast food dining
[9 empty] | Classrooms (ages 5-8) | Cell
[9 empty] | Coffee stations | Classrooms (age 9 plus)
[9 empty] | Coin-operated laundries | Classrooms (ages 5-8)
[9 empty] | Common corridors | Coffee stations
[9 empty] | Computer (not printing ) | Coin-operated laundries
[9 empty] | Computer lab | Common corridors
[9 empty] | Conference / meeting | Computer (not printing )
[9 empty] | Corridors | Computer lab
[9 empty] | Courtrooms | Conference / meeting
[9 empty] | Day room | Corridors
[9 empty] | Daycare (through age 4) | Courtrooms
[9 empty] | Daycare sickroom | Day room
[9 empty] | Disco / dance floors | Daycare (through age 4)
[9 empty] | Dwelling unit | Disco / dance floors
[9 empty] | Electrical equipment rooms | Dwelling unit - studio or one-bedroom
[9 empty] | Elevator machine rooms | Dwelling unit - three-bedroom
[9 empty] | Gambling casinos | Dwelling unit - two-bedroom
[9 empty] | Game arcades | Gambling casinos
[9 empty] | Guard stations | Game arcades
[9 empty] | Gym, stadium (play area) | General manufacturing (excludes heavy industrial and processes using chemicals)
[9 empty] | Health club / aerobics | Guard stations
[9 empty] | Health club / weight | Gym, stadium (play area)
[9 empty] | Laundry rooms within dwelling units | Health club / aerobics
[9 empty] | Laundry rooms, central | Health club / weight
[9 empty] | Lecture classroom | Kitchen (cooking)
[9 empty] | Lecture hall (fixed seats) | Laundry rooms within dwelling units
[9 empty] | Legislative chambers | Laundry rooms, central
[9 empty] | Libraries | Lecture classroom
[9 empty] | Lobbies | Lecture hall (fixed seats)
[9 empty] | Lobbies / prefunction | Legislative chambers
[9 empty] | Main entry lobbies | Libraries
[9 empty] | Mall common areas | Lobbies
[9 empty] | Media center | Lobbies / prefunction
[9 empty] | Multi-purpose assembly | Main entry lobbies
[9 empty] | Multi-use assembly | Mall common areas
[9 empty] | Museums (children's) | Media center
[9 empty] | Museums / galleries | Multi-purpose assembly
[9 empty] | Music / theater/ dance | Multi-use assembly
[9 empty] | Office space | Museums (children's)
[9 empty] | Pet shops | Museums / galleries
[9 empty] | Pharmacy (prep, area) | Music / theater/ dance
[9 empty] | Photo studios | Occupiable storage rooms for dry materials
[9 empty] | Places of religious worship | Occupiable storage rooms for liquids or gels
[9 empty] | Reception areas | Office space
[9 empty] | Restaurant dining rooms | Pet shops (animal areas)
[9 empty] | Sales | Pharmacy (prep, area)
[9 empty] | Science laboratories | Photo studios
[9 empty] | Shipping / receiving | Places of religious worship
[9 empty] | Spectator areas | Reception areas
[9 empty] | Sports arena (play area) | Restaurant dining rooms
[9 empty] | Stages, studios | Sales
[9 empty] | Storage rooms | Science laboratories
[9 empty] | Supermarket | Shipping / receiving
[9 empty] | Swimming (pool & deck) | Sorting, packing, light assembly
[9 empty] | Telephone / data entry | Spectator areas
[9 empty] | Transportation waiting | Sports arena (play area)
[9 empty] | Warehouses | Stages, studios
[9 empty] | Wood / metal shop | Supermarket
Swimming (pool & deck)
Telephone / data entry
Telephone closets
Transportation waiting
University / college laboratories
Warehouses
Wood / metal shop
[9 empty] | max Zpz | Ev
[9 empty] | 0 | 1
[9 empty] | 0.01 | 1
[9 empty] | 0.02 | 1
[9 empty] | 0.03 | 1
[9 empty] | 0.04 | 1
[9 empty] | 0.05 | 1
[9 empty] | 0.06 | 1
[9 empty] | 0.07 | 1
[9 empty] | 0.08 | 1
[9 empty] | 0.09 | 1
[9 empty] | 0.1 | 1
[9 empty] | 0.11 | 1
[9 empty] | 0.12 | 1
[9 empty] | 0.13 | 1
[9 empty] | 0.14 | 1
[9 empty] | 0.15 | 1
[9 empty] | 0.16 | 0.99
[9 empty] | 0.17 | 0.98
[9 empty] | 0.18 | 0.97
[9 empty] | 0.19 | 0.96
[9 empty] | 0.2 | 0.95
[9 empty] | 0.21 | 0.94
[9 empty] | 0.22 | 0.93
[9 empty] | 0.23 | 0.92
[9 empty] | 0.24 | 0.91
[9 empty] | 0.25 | 0.9
[9 empty] | 0.26 | 0.89
[9 empty] | 0.27 | 0.88
[9 empty] | 0.28 | 0.87
[9 empty] | 0.29 | 0.86
[9 empty] | 0.3 | 0.85
[9 empty] | 0.31 | 0.84
[9 empty] | 0.32 | 0.83
[9 empty] | 0.33 | 0.82
[9 empty] | 0.34 | 0.81
[9 empty] | 0.35 | 0.8
[9 empty] | 0.36 | 0.79
[9 empty] | 0.37 | 0.78
[9 empty] | 0.38 | 0.77
[9 empty] | 0.39 | 0.76
[9 empty] | 0.4 | 0.75
[9 empty] | 0.41 | 0.74
[9 empty] | 0.42 | 0.73
[9 empty] | 0.43 | 0.72
[9 empty] | 0.44 | 0.71
[9 empty] | 0.45 | 0.7
[9 empty] | 0.46 | 0.69
[9 empty] | 0.47 | 0.68
[9 empty] | 0.48 | 0.67
[9 empty] | 0.49 | 0.66
[9 empty] | 0.5 | 0.65
[9 empty] | 0.51 | 0.64
[9 empty] | 0.52 | 0.63
[9 empty] | 0.53 | 0.62
[9 empty] | 0.54 | 0.61
[9 empty] | 0.55 | 0.6
Delete System
Add System

## Multiple Zone (hidden)
| Multiple zone | [22 empty] | Floor area | Population | Rp | Ra | D | Ez average | Ev | Vps | Xs | Required Vot | Actual
| #VALUE! | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Show simple view | [21 empty] | TRUE
| System name and number |  | #VALUE!
Condition analyzed (impacts Ez, Vdz, Vpz and Vps)
All zones are included in the VRP calculation
| Zone Name and Number | Occupancy Category |  | Zone Floor Area | Are you using default value for zone population? | Zone Population | People Outdoor Air Rate | Area Outdoor Air Rate | Breathing Zone Outdoor Airflow (people related portion) | Breathing Zone Outdoor Airflow (area related portion) | Breathing Zone Outdoor Airflow | Zone Air Distribution Effectiveness | Zone Outdoor Airflow | Zone Discharge Airflow | Zone Primary Airflow | Primary Outdoor Air Fraction | Zone Secondary Recirculation Fraction | Zone Primary Air Fraction | Supply Air Fraction | Mixed Air Fraction | Outdoor Air Fraction | Zone Ventilation Efficiency (Appendix A) | Default Pz | Nondefault Pz | Occupant Density | Zone name for critical zone lookup
|  |  |  | Az |  | Pz | Rp | Ra |  |  | Vbz | Ez | Voz | Vdz | Vpz | Zpz | Er | Ep | Fa | Fb | Fc | Evz
|  |  |  | (sq ft) |  | (people) | (cfm per person) | (cfm per sq ft) | (cfm) | (cfm) | Vbz: (cfm); Voz: (cfm); Vdz: (cfm); Vpz: (cfm) |  |  | (occupants per 1,000 sq ft)
A | [8 empty] | Rp Pz | Ra Az | (Rp Pz + Ra Az)*1.3 |  | Vbz / Ez |  |  | Voz / Vpz |  | Vpz/Vdz | Ep + (1-Ep) Er | Ep | 1-(1-Ez)(1-Er)(1-Ep) | (Fa+Xs * Fb-Zpz *Ep*Fc)/Fa
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[23 empty] | all zones | critical zones
| System area | As | (sq ft) | 0 | ∑Az | [17 empty] | 0
| System population | Ps | (people)
| Sum of zone population | sum of Pz | (people) | 0 | ∑Pz
| Occupant diversity | D |  | 0 | Ps / ∑Pz
| People outdoor air rate for system | Rp system | (cfm per person)
| Area outdoor air rate for system | Ra system | (cfm per sq ft)
| Uncorrected outdoor air intake | Vou | (cfm) | 0 | ((Rp system Ps) + (Ra system As))*1.3
| System primary airflow (at condition analyzed) | Vps | (cfm)
| Average outdoor air fraction | Xs |  | 0 | Vou / Vps
Which method from ASHRAE 62.1 is being used to determine system ventilation efficiency (Ev)?
| Max (Zpz) | Max Zpz |  | 0
| Zone ventilation efficiency (Table 6-3) | Evz |  | 0
| Minimum (Evz) |  |  | 0
| Critical zone |  |  | 0 | [18 empty] | Not other | Other
| Ventilation efficiency | Ev | [20 empty] | 0
| Outdoor air intake flow (30% above 62.1 requirement) | Vot | (cfm) | 0 | Vou / Ev
| Outdoor air intake flow provided (measured or design) |  | (cfm)
Note on B21: Simultaneous number of occupants in the area served by the ventilation system
Note on B24: Area-weighted Rp value
Note on B25: People-weighted Ra value
Note on B27: Highest expected system primary airflow at the condition analyzed (usually less than ∑Vpz, since primary airflow seldom peaks simultaneously in all VAV zones)
Note on B31: Largest value of Zpz
Note on B32: Lookup from ASHRAE 62.1, Table 6-3
Note on B33: Lowest zone ventilation efficiency among all zones served by the air handler
Note on B34: If using Table 6-3 to determine Ev, the critical zone is the zone with largest value of Zpz. Otherwise, the critical zone is the zone with minimum Evz value.
Note on C10: From ASHRAE 62.1, Table 6-1
Note on E10: Net occupiable floor area of the ventilation zone
Note on F10: The default value should only be used if the expected occupancy is unknown.
Note on G10: Number of people in the ventilation zone during typical usage
Note on H10: Outdoor airflow rate required per person as determined from ASHRAE 62.1, Table 6-1
Note on I10: Outdoor airflow rate required per unit as determined from ASHRAE 62.1, Table 6-1
Note on M10: Measure of effectiveness of supply air distribution to the breathing zone. See Instructions tab for recommended Ez values.
Note on O10: Expected discharge (supply) airflow to the zone that includes primary airflow and secondary recirculated airflow
Note on P10: Primary airflow rate to the ventilation zone from the air handler, including outdoor air and recirculated air. (for VAV-system design purposes, Vpz is lowest zone primary airflow value expected at the design condition analyzed.)
Note on R10: Fraction of secondary recirculated air to the zone that is representative of average system return air rather than air directly recirculated from the zone. See Instructions tab for recommended Er values.
Note on S10: The fraction of primary air in the discharge air to the ventilation zone (Vpz / Vdz). For single-zone and single-supply systems, Ep is 1.0.
Add Rows
Delete Rows

## 100% OA (hidden)
| 100% Outdoor air | [13 empty] | >>>> | >>>> | >>>> | >>>> | >>>> | >>>> | >>>> | >>>> | >>>> | >>>> | Floor area | Population | Rp | Ra | D | Ez average | Ev | Vps | Xs | Required Vot | Actual
| #VALUE! | [23 empty] | 0 | 0 | 0 | 0 | n/a | 0 | n/a | n/a | n/a | 0 | 0
| Show simple view | [13 empty] | TRUE
| System name and number |  | #VALUE!
| Condition analyzed (impacts Ez) | [35 empty] | 0 | 0 | Yes
| Zone Name and Number | Occupancy Category |  | Zone Floor Area | Are you using default value for zone population? | Zone Population | People Outdoor Air Rate | Area Outdoor Air Rate | Breathing Zone Outdoor Airflow (people related portion) | Breathing Zone Outdoor Airflow (area related portion) | Breathing Zone Outdoor Airflow | Zone Air Distribution Effectiveness | Zone Outdoor Airflow | Zone Outdoor Airflow Provided | Default Pz | Default Pz | Occupant Density
|  |  |  | Az |  | Pz | Rp | Ra |  |  | Vbz | Ez | Voz | (measured or design)
B |  |  |  | (sq ft) |  | (people) | (cfm per person) | (cfm per sq ft) | (cfm) | (cfm) | (cfm) |  | (cfm) | (cfm)
A | [8 empty] | Rp Pz | Ra Az | (Rp Pz + Ra Az)*1.3 |  | Vbz / Ez |  |  |  | (occupants per 1,000 sq ft)
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [18 empty] | Yes
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [18 empty] | Yes
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [18 empty] | Yes
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [18 empty] | Yes
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | [18 empty] | Yes
| System area (sq ft) | As | (sq ft) | 0 | ∑Az
| System population | Ps | (people) | 0 | ∑Pz
| Outdoor air intake flow (30% above 62.1 requirement) | Vot | (cfm) | 0 | ∑Voz
| Outdoor air intake flow provided (measured or design) |  | (cfm)
Note on C9: Lookup from ASHRAE 62.1, Table 6-1
Note on E9: Net occupiable floor area of the ventilation zone
Note on F9: The default value should only be used if the expected occupancy is unknown.
Note on G9: Number of people in the ventilation zone during typical usage
Note on H9: Outdoor airflow rate required per person as determined from ASHRAE 62.1, Table 6-1
Note on I9: Outdoor airflow rate required per unit as determined from ASHRAE 62.1, Table 6-1
Note on M9: Measure of effectiveness of supply air distribution to the breathing zone
Add Rows
Delete Rows

## Single Zone (hidden)
Single zone
Single Zone
| Show simple view | [11 empty] | FALSE
| System Name and Number | Condition Analyzed (impacts Ez) | Occupancy Category | Zone Floor Area | Are you using default value for zone population? | Zone Population | People Outdoor Air Rate | Area Outdoor Air Rate | Breathing Zone Outdoor Airflow | Zone Air Distribution Effectiveness | Zone Outdoor Airflow | Outdoor air intake flow provided (measured or design) | Default Pz | Nondefault Pz | Occupant Density
|  |  |  | Az |  | Pz | Rp | Ra | Vbz | Ez | Voz
B |  |  |  | (sq ft) |  | people | (cfm per person) | (cfm per sq ft) | (cfm) |  | (cfm) | (cfm) |  |  | Occupants per 1,000 sq ft
[9 empty] | (Rp Pz + Ra Az)*1.3 |  | Vbz / Ez
HIDDEN SPACER FOR SUMMARY
0 | [6 empty] | 0 | 0 | 0 |  | 0 |  | 0 |  | 0
0 | residential | Heating | Dwelling unit - three-bedroom | 300 | No | 5 | 5 | 0.06 | 55.9 | 0.8 | 69.875 |  | 1.2 |  | 4
Note on D7: Lookup from ASHRAE 62.1, Table 6-1
Note on E7: Net occupiable floor area of the ventilation zone
Note on F7: The default value should only be used if the expected occupancy is unknown.
Note on G7: Number of people in the ventilation zone during typical usage
Note on H7: Outdoor airflow rate required per person as determined from ASHRAE 62.1, Table 6-1
Note on I7: Outdoor airflow rate required per unit as determined from ASHRAE 62.1, Table 6-1
Note on K7: Measure of effectiveness of supply air distribution to the breathing zone
Add System
Delete System

## LU Office
| Multiple zone | [22 empty] | Floor area | Population | Rp | Ra | D | Ez average | Ev | Vps | Xs | Required Vot | Actual
| #VALUE! | [22 empty] | 4270 | 14 | 5 | 0.063091 | 0.36 | 0.825 | 0.84 | 4040 | 0.1 | 523 | 0
| Show simple view | [21 empty] | TRUE
| System name and number |  | #VALUE!
| Condition analyzed (impacts Ez, Vdz, Vpz and Vps) |  | Heating
| All zones are included in the VRP calculation |  | Yes
| Zone Name and Number | Occupancy Category |  | Zone Floor Area | Are you using default value for zone population? | Zone Population | People Outdoor Air Rate | Area Outdoor Air Rate | Breathing Zone Outdoor Airflow (people related portion) | Breathing Zone Outdoor Airflow (area related portion) | Breathing Zone Outdoor Airflow | Zone Air Distribution Effectiveness | Zone Outdoor Airflow | Zone Discharge Airflow | Zone Primary Airflow | Primary Outdoor Air Fraction | Zone Secondary Recirculation Fraction | Zone Primary Air Fraction | Supply Air Fraction | Mixed Air Fraction | Outdoor Air Fraction | Zone Ventilation Efficiency (Appendix A) | Default Pz | Nondefault Pz | Occupant Density | Zone name for critical zone lookup
|  |  |  | Az |  | Pz | Rp | Ra |  |  | Vbz | Ez | Voz | Vdz | Vpz | Zpz | Er | Ep | Fa | Fb | Fc | Evz
|  |  |  | (sq ft) |  | (people) | (cfm per person) | (cfm per sq ft) | (cfm) | (cfm) | Vbz: (cfm); Voz: (cfm); Vdz: (cfm); Vpz: (cfm) |  |  | (occupants per 1,000 sq ft)
A | [8 empty] | Rp Pz | Ra Az | (Rp Pz + Ra Az)*1.3 |  | Vbz / Ez |  |  | Voz / Vpz |  | Vpz/Vdz | Ep + (1-Ep) Er | Ep | 1-(1-Ez)(1-Er)(1-Ep) | (Fa+Xs * Fb-Zpz *Ep*Fc)/Fa
0 | [6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | Office 1 | Office space |  | 150 | No | 1 | 5 | 0.06 | 5 | 9 | 18.2 | 0.8 | 22.75 | 500 | 220 | 0.1 | 0.75 | 0.44 | 0.86 | 0.44 | 0.97 | 1 | 0.75 |  | 5 | Office 1
0 | Office 2 | Office space |  | 150 | No | 1 | 5 | 0.06 | 5 | 9 | 18.2 | 0.8 | 22.75 | 500 | 220 | 0.1 | 0.75 | 0.44 | 0.86 | 0.44 | 0.97 | 1 | 0.75 |  | 5 | Office 2
0 | Office 3 | Office space |  | 200 | No | 2 | 5 | 0.06 | 10 | 12 | 28.6 | 0.8 | 35.75 | 500 | 220 | 0.16 | 0.75 | 0.44 | 0.86 | 0.44 | 0.97 | 0.97 | 1 |  | 5 | Office 3
0 | Breakroom | Breakrooms (office buildings) |  | 220 | No | 4 | 5 | 0.12 | 20 | 26.4 | 60.32 | 0.8 | 75.4 | 1000 | 560 | 0.13 | 0.75 | 0.56 | 0.89 | 0.56 | 0.97 | 0.98 | 11 |  | 50 | Breakroom
0 | Conference 1 | Conference / meeting |  | 850 | No | 14 | 5 | 0.06 | 70 | 51 | 157.3 | 1 | 157.3 | 500 | 500 | 0.31 | 0.75 | 1 | 1 | 1 | 1 | 0.79 | 42.5 |  | 50 | Conference 1
0 | Conference 2 | Conference / meeting |  | 420 | No | 6 | 5 | 0.06 | 30 | 25.2 | 71.76 | 0.8 | 89.7 | 1000 | 560 | 0.16 | 0.75 | 0.56 | 0.89 | 0.56 | 0.97 | 0.96 | 21 |  | 50 | Conference 2
0 | Open Office | Office space |  | 1960 | No | 10 | 5 | 0.06 | 50 | 117.6 | 217.88 | 0.8 | 272.35 | 2160 | 1320 | 0.21 | 0.75 | 0.61111 | 0.9 | 0.61 | 0.98 | 0.92 | 9.8 |  | 5 | Open Office
0 | Corridors | Corridors |  | 320 | No | 0 | 0 | 0.06 | 0 | 19.2 | 24.96 | 0.8 | 31.2 | 720 | 440 | 0.07 | 0.75 | 0.61111 | 0.9 | 0.61 | 0.98 | 1.02 | 0 |  | 0 | Corridors
[23 empty] | all zones | critical zones
| System area | As | (sq ft) | 4270 | Net occupiable floor area served by the ventilation system | [17 empty] | 4270
| System population | Ps | (people) | 14
| Sum of zone population | sum of Pz | (people) | 38 | ∑Pz
| Occupant diversity | D |  | 0.36 | Ps / ∑Pz
| People outdoor air rate for system | Rp system | (cfm per person) | 5
| Area outdoor air rate for system | Ra system | (cfm per sq ft) | 0.06
| Uncorrected outdoor air intake | Vou | (cfm) | 439.14 | (D ∑ (Rp Pz) + ∑(Ra Az))*1.3
| System primary airflow (at condition analyzed) | Vps | (cfm) | 4040
| Average outdoor air fraction | Xs |  | 0.1 | Vou / Vps
| Which method from ASHRAE 62.1 is being used to determine system ventilation efficiency (Ev)? |  |  | Table 6-3
| Max (Zpz) | Max Zpz |  | 0.31
| Zone ventilation efficiency (Table 6-3) | Evz |  | 0.84
| Minimum (Evz) |  |  | 0.79
| Critical zone |  |  | Conference 1 | [18 empty] | Not other | Other
| Ventilation efficiency | Ev |  | 0.84 | Ventilation efficiency from critical zone | [17 empty] | 0.84
| Outdoor air intake flow (30% above 62.1 requirement) | Vot | (cfm) | 522.7857 | Vou / Ev
| Outdoor air intake flow provided (measured or design) |  | (cfm)
Note on B29: Area-weighted Rp value
Note on B30: People-weighted Ra value
Note on B32: Highest expected system primary airflow at the condition analyzed (usually less than ∑Vpz, since primary airflow seldom peaks simultaneously in all VAV zones)
Note on B36: Largest value of Zpz
Note on B37: Lookup from ASHRAE 62.1, Table 6-3
Note on B38: Lowest zone ventilation efficiency among all zones served by the air handler
Note on B39: If using Table 6-3 to determine Ev, the critical zone is the zone with largest value of Zpz. Otherwise, the critical zone is the zone with minimum Evz value.
Note on C10: From ASHRAE 62.1, Table 6-1
Note on E10: Net occupiable floor area of the ventilation zone
Note on F10: The default value should only be used if the expected occupancy is unknown.
Note on G10: Number of people in the ventilation zone during typical usage
Note on H10: Outdoor airflow rate required per person as determined from ASHRAE 62.1, Table 6-1
Note on I10: Outdoor airflow rate required per unit as determined from ASHRAE 62.1, Table 6-1
Note on M10: Measure of effectiveness of supply air distribution to the breathing zone. See Instructions tab for recommended Ez values.
Note on O10: Expected discharge (supply) airflow to the zone that includes primary airflow and secondary recirculated airflow
Note on P10: Primary airflow rate to the ventilation zone from the air handler, including outdoor air and recirculated air. (for VAV-system design purposes, Vpz is lowest zone primary airflow value expected at the design condition analyzed.)
Note on R10: Fraction of secondary recirculated air to the zone that is representative of average system return air rather than air directly recirculated from the zone. See Instructions tab for recommended Er values.
Note on S10: The fraction of primary air in the discharge air to the ventilation zone (Vpz / Vdz). For single-zone and single-supply systems, Ep is 1.0.
Add Rows
Delete Rows

## Summary
1
| 1 | Summary
| 1 | Note: All information on this tab is READ-ONLY. To edit, see the previous tab(s).
| 1 | [17 empty] | TRUE
| 1 |  | Show simple view
1
| 1 | System Name and Number | System Type | All zones included in the VRP calculation? | Condition Analyzed | System Floor Area | System Population | Outdoor Air Intake Flow (30% above 62.1 requirement) | Outdoor Air Intake Flow Provided (measured or design) | Outdoor air intake flow provided meets or exceeds Vot? | People Outdoor Air Rate for System | Area Outdoor Air Rate for System | Occupant Diversity D | Average Zone Air Distribution Effectiveness Ez average | Ventilation Efficiency Ev | System Primary Airflow (at condition analyzed) | Average Outdoor Air Fraction Xs | Zone outdoor airflow provided meets or exceeds Voz for all zones?
B | [5 empty] | As | Ps | Vot |  |  | Rp system | Ra system |  |  |  | Vps
| 1 |  |  |  |  | (sq ft) | (people) | (cfm) | (cfm) |  | (cfm per person) | (cfm per sq ft) |  |  |  | (cfm)
Single Zone Systems
|  | 0 | Single zone | n/a | 0 | 0 | 0 | 0 | 0 | No | 0 | 0 | n/a | 0 | n/a | n/a | n/a | n/a
|  | residential | Single zone | n/a | Heating | 300 | 5 | 70 | 0 | No | 5 | 0.06 | n/a | 0.8 | n/a | n/a | n/a | n/a
Multiple Zone Systems
| 0 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | n/a
| 0 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | n/a
A
100% Outdoor Air Systems
| 0 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
C
|  | Totals |  |  |  | #NAME? | #NAME? | #NAME? | #NAME? | [6 empty] | #NAME?
Refresh Systems